Apstar

Limited

In Control since 1988

GembusHub Modbus Datamap

Unit 7

North Staffs Enterprise Centre

Innovation Way

Stoke on Trent

ST6 4BF

England

+44 1782 834177

mail@apstar.co.uk

www.gembushub.com

- Issue 008 9 April 2024

- © Apstar Limited

This document is intended for System Installers. It contains the detailed technical information needed to access and setup the GembusHub.

# Revision History:

| Revision | Date | Comment |
| --- | --- | --- |
| Pre-release history |  |  |
| A | 14/11/14 | First draft of Modbus Memory Map. |
| B | 6/2/15 | Updated Configuration data map Added multi access to Input Data. Allocated the address map for the GembusHub data. |
| C | 19/3/15 | Updates to the Link statistics as details were coded. Changed the device addresses from 10 to 14 to 16 to 20 to avoid using the CR and LF characters as addresses. GembusHub Statistics moved from 200 to 500 to make space for settings. Moved Configuration change counts to 5200 and made them fully accessible. Moved ConfigCRC to 5100, also fully accessible. Moved read only GembusHub Status/Statistics variables out into a separate memory array. Removed fixed IP address option. |
| D | 25/3/15 | - Added “fixed IP address” back in again. - Rearranged the 100 range registers to allow the configuration of fixed IP address, router address and the net mask. - Added the actual address used at address 513. - Added example of Modbus accesses to chapter 2. |
| E | 28/4/15 | - Added 618, count of invalid IP address accesses. - Added section 5.8.1, remote reboot - Added Gemstart simulator – Set Control (106-109) = 12321. - Added Status Registers Written array at 4600. - GembusHub tested to this document from 23/4/15 to 28/4/15. Faults fixed and document updated along the way. This version of the document released after testing and firmware 2.60.1.2 released as a reference point. |
| F | 12/05/15 | - Added register 207 to test LEDs. - Copied register 1101 status to 512 as well. - MAC address used to identify boards so no separate serial number required (registers 507, 508) - Added GembusHub LED indication via Modbus (525 to 530). - Moved Data Size and broadcast settings from link control to link settings. (1301 and 1302 moved to 1007 and 1008) |
| G | 18/6/15 | - Added the CRC to the end of the configuration data read. You can - read length 120 to get just the configuration or length 121 to get configuration and the CRC. |
| H | 14/7/15 | - Added the Gemstart type info at address 6000 to 6099. The - Development Data at 6000 has been moved to address 7000. |
| Released versions |  |  |
| 001 | 15/07/2015 | Initial Customer Release |
| 002 | 23/09/2015 | Scratchpad area added to device 16 address 9000 length 512 Cosmetic changes to some text items - V4.60.1.9. Added ability to connect a Modbus Host to one of the RS485 ports by setting register 106 to 109 to 10. - Ethernet Timeout changed to PLC Control Timeout. Timeout action is now only taken if no Modbus messages on Ethernet or RS485. |

| 003 | - 17/02/2016: - GembusHub - 4.60.1.10 | - Updated description to registers 110, 113-125. Changing these registers now restarts the Ethernet interface. - Updated register 126. The permitted IP addresses are now checked dynamically and not just at connection. - Register 511 bit 3 no longer relevant. - Added register 623: The rejected connection port - Updated description in 5.4.2, Single Data Request - Added register 1319, Requested Data Length |
| --- | --- | --- |
| 004 | - 25/02/2015 - GembusHub - 4.60.1.11 | - If the Control Link fails and Link Control is set to 1 then Link Control is changed to 0 to stop Gembus Comms. The PLC must set the Link Control to 1 again after the Control Link is re-established. |
| 005 | - 19/02/2020 - 4.60.2.4 | - Added Single Data Request timing info. (4.60.1.12) - Removed baud rates above 38,400 for Gembus and Modbus. (4.60.2.3) - Added TCP/IP statistics in tables 624 to 634. (4.60.2.4) |
| 006 | - 05/08/2023 - 4.60.2.5 | - Added 511 bit 4: set while there are Serial Flash Memory CRC errors. - Added 635: count of serial flash memory writes. - Added 636: number of serial flash readback CRC errors |
| 007 | - 20/02/2024 - 4.60.2.6 | - Added 208 to define which Modbus IP connections are PLC Control devices. Only these devices will reset the Control Timeout with Modbus messages. Updated the description for register 111. |
| 008 | - 09/04/2024 - 4.60.2.8 | - Gemstart type, 6000 registers, can now be written to to clear old data types. |

# Contents

Revision History:	1

1	Contents	4

2	GembusHub Modbus Memory Map	6

2.1	GembusHub Data Summary	6

2.2	Gemstart Link Data Summary	6

2.3	Modbus Functions	7

2.4	Principles of Operation	7

3	Modbus TCP/IP	8

4	USB	9

4.1	Modbus via USB	9

5	GembusHub Registers	10

5.1	GembusHub Settings	10

5.2	GembusHub Info	13

5.3	GembusHub Statistics	15

6	Gembus Registers	17

6.1	Link Settings	17

6.1.1	Broadcast Control	18

6.1.2	Continuous Data Request Control	18

6.2	Link Statistics	19

6.3	Gemstart Status Flags	20

6.4	Link Controls	21

6.4.1	Group Control	21

6.4.2	Single Data Request	22

6.5	Output Command Array	24

6.6	Input Data Array	24

6.7	Configuration Data	26

6.7.1	Config CRCs	26

6.7.2	Configuration Change Counts	27

6.7.3	Gemstart Type	27

6.8	Development Data	28

6.9	Scratchpad	29

# GembusHub Modbus Memory Map

GembusHub is a communications device capable of supporting 400 Gemstarts across 4 links of up to 100 Gemstarts each. GembusHub makes available all the information from these Gemstarts in a Modbus data map accessible using the Modbus TCP/IP protocol. The same address map is provided via the USB port although Serial Modbus is used for this access route.

GembusHub has lots of data to maintain. All data is available using Word Reads. Some data can be written to but may be read only and will not change. Some data ranges cannot be written to at all. There are separate data areas for the GembusHub and each of the Gemstart Links. The device address is used to specify the target data area.

The data areas are split as follows:

|  | Modbus TCP/IP Unit Identifier | Serial Modbus Device Address |
| --- | --- | --- |
| GembusHub Data | 16 (0x10) | 16 (0x10) |
| Gemstart Link 1 Data | 17 (0x11) | 17 (0x11) |
| Gemstart Link 2 Data | 18 (0x12) | 18 (0x12) |
| Gemstart Link 3 Data | 19 (0x13) | 19 (0x13) |
| Gemstart Link 4 Data | 20 (0x14) | 20 (0x14) |

## GembusHub Data Summary

This data relates to the GembusHub as a whole.

- Address 100 - GembusHub Settings

- Address 500 - GembusHub Info

- Address 600 - GembusHub Statistics

## Gemstart Link Data Summary

This data relates to one link of Gemstarts. A separate set of data is available at the 4 devices station addresses (17-20) used for the four ports.

- Address 1000 - Link Settings

- Address 1100 - Link Statistics

- Address 1200 - Status Flags

- Address 1300 - Link Control Registers

- Address 2000 - Output Commands Array

- Address 3000 - Input Data Array

- Address 5000 - Configuration Data

## Modbus Functions

The following Modbus functions are implemented on TCP/IP and USB

3, Read Holding Registers

4, Read Input Registers

6, Write Single Register

16, Write Multiple Registers

The Holding Registers and the Input Registers access the same data map. There is no difference in how these two functions work.

Additional Information

Max Register Read or Write Length is 123 registers

Modbus register addressing is defined as 1 to 65536. In the low level comms the address offset from 1 is used. So this document refers to the Modbus Address (range 1 to 65536). The tables below contain the Modbus addresses (1-65536).

## Principles of Operation

Once the unit has been set up it will continuously poll the Gemstart devices and retain the status and configuration data for all of the Gemstart units. This information is made available to the system via the Modbus TCP/IP interface and also via the USB port if any local access is required.

GembusHub is capable of hosting Gemstart 1’s, 2’s and 3’s on the same link as Gemstart 4’s and 5’s. It is recommended that if Gemstart 1, 2 or 3 are on the link then link number 0 is used.

The content of data returned by each Gemstart type will be defined by that Gemstart. To decode the data correctly please refer to the documentation for the Gemstart model in question.

This is the same for the content of any command sent to an attached Gemstart unit, please refer to the appropriate documentation to ensure the correct data is sent to each Gemstart.

# Modbus TCP/IP

Modbus over TCP/IP allows standard Modbus messages to be sent across a TCP/IP network such as Ethernet.

GembusHub is a Modbus Server. This means that it is a passive device that responds to messages from a client. It is up to the client to initiate all data transfers. Up to 20 Modbus requests can be sent at the same time either from different IP addresses or from different ports within each IP address. Each port of an IP address can only action 1 message at a time.

For example if GembusHub is accessed from the Modbus Poll program then only one read at a time can be actioned as only one port is used to access the GembusHub. Starting a second and third instance of the Modbus Poll program then multiple ports are created allowing 3 parallel accesses to GembusHub. If 3 or more Modbus Poll programs are started on another PC then another 3 or more parallel access paths are possible into Gemstart Hub. All in all, 20 separate programs can be accessing the GembusHub data at one time, plus 1 channel used by a program accessing GembusHub data via the USB port, plus up to 4 Modbus connections using the RS485 ports and Modbus RTU.

When GembusHub is first connected to the network it is allocated an IP address either from the fixed address defined in the settings or allocated by the DHCP server. An address allocated by DHCP address should be fixed. Ie the same unit is always allocated the same IP address. This will allow a PLC to know exactly which GembusHub it is accessing for a given IP address. As a confirmation, a PLC should always read and check the MAC address which can be read in registers 508 to 510.

The control system can read the GembusHub MAC address from the GembusHub to verify that the expected GembusHub is connected. The IP address and the GembusHub MAC address can also be read via the GembusHub USB port.

All Modbus TCP/IP messages have a MBAP header that replaces the header and checksum that are part of a normal Modbus message. The standard header contains the Slave Address. This is replaced with the Unit Identifier. The Unit Identifier is used to define which area of GembusHub is being addressed.

MBAP Header (Big Endian Data Order = High Byte Low Memory)

| Byte | Description | Range | Comments |
| --- | --- | --- | --- |
| 0&1 | Transaction Identifier | 0-65535 | Echoed by GembusHub |
| 2&3 | Protocol Identifier | 0 | 0 identifies Modbus. Message ignored if this is not 0. |
| 4&5 | Message Length |  | The size of the combined unit identifier, function code and data message following the header |
| 6 | Unit Identifier | 16-20 | 16: (0x10) GembusHub Registers 17-20: (0x11-0x14) Gembus ports 1 to 4. |

All Modbus TCP/IP messages use port 502 (configurable).

# USB

GembusHub will appear as a standard COM port on the PC. An .inf file may have to be selected the first time the USB port is connected.

## Modbus via USB

The USB com port can be used as a MODBUS port with Modbus device address 0x10 (16) for GembusHub registers and addresses 0x11-0x14 (17-20) for Gembus ports 1 to 4.

# GembusHub Registers

GembusHub registers are accessed via Modbus station address 0x10.

There are a number of settings that are defined for the whole unit and statistics that relate to the whole unit rather that the individual ports. These configuration registers and statistics are defined here.

## GembusHub Settings

Theses settings define how the GembusHub operates. All of them are read/write and are retained through a power cycle. Only the date and time are changed by GembusHub although the Link Control registers may be modified after a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 100 | Day | 1-31 | Set the date and time. Not retained through a power down. |
| 101 | Month | 1-12 |  |
| 102 | Year | 0-99 |  |
| 103 | Hour | 0-23 |  |
| 104 | Minute | 0-59 |  |
| 105 | Second | 0-59 |  |
| 106 | Link 1 Control | 0-10 | 0 = No transmissions 1 = Transmission enabled while PLC in control but disabled by a PLC Control Timeout or GembusHub power cycle (ie changes to 0 on a timeout or power cycle) Must be written to 1 or 2 to restart the link 2 = Transmission auto enabled after a link recovery or power cycle. After power on all commands changed to No Action. Then the PLC Timeout Action is taken. 10 = Modbus Slave for connection to PLC master |
| 107 | Link 2 Control | 0-2 | As above |
| 108 | Link 3 Control | 0-2 | As above |
| 109 | Link 4 Control | 0-2 | As above |
| 110 | Modbus TCPIP Port | 502 | Default for Modbus TCP/IP is 502. Changing this value causes an automatic restart of the ethernet port, this can be up to 4 seconds. |
| 111 | PLC Control Timeout time (ms) | 0-65535 | R/W. PLC Control Timeout time in ms. If no Ethernet or RS485 Modbus message is received within this time then the PLC Control Timeout Action is taken. Must be non zero to enable this feature. See 126 and 208 for selecting which Ethernet Modbus connections are allowed and which reset the PLC Control Timeout timer. |

| 112 | PLC Control Timeout Action | 0-3 | Only relevant if Link Control is set to 2 0 = Keep running 1 = Keep running and change all command to No Action. 2 = Keep running and change all commands to Stop. 3 = Stop the Gembus Comms. Set commands to No Action. Allows each Gemstart to take its own link fail action. On restart the PLC can update the commands. If Link Control is set to 1 the Commands are updated as above and Link Control is changed to 0 which stops Tx. |
| --- | --- | --- | --- |
| 113 | Define IP Address | 0-1 | Define how the IP address is obtained. 0 Get IP address from DHCP 1 Use the fixed IP details defined below Changing this value causes an automatic restart of the ethernet port, this can be up to 4 seconds. |
| 114 | Fixed IP Address byte 1 | 0-255 | Only relevant if “Define IP Address” is set to 1. GembusHub address eg 192.168.1.2 Changing this value when a fixed address is specified causes an automatic restart of the ethernet port, this can be up to 4 seconds. |
| 115 | Fixed IP Address byte 2 | 0-255 |  |
| 116 | Fixed IP Address byte 3 | 0-255 |  |
| 117 | Fixed IP Address byte 4 | 0-255 |  |
| 118 | Router Address byte 1 | 0-255 | Only relevant if “Define IP Address” is set to 1. Router address eg 192.168.1.1 Messages not within the Net Mask are sent to the router. Changing this value when a fixed address is specified causes an automatic restart of the ethernet port, this can be up to 4 seconds. |
| 119 | Router Address byte 2 | 0-255 |  |
| 120 | Router Address byte 3 | 0-255 |  |
| 121 | Router Address byte 4 | 0-255 |  |
| 122 | Net Mask byte 1 | 0-255 | Only relevant if “Define IP Address” is set to 1. The mask for the addresses on this network eg 255.255.255.0 Messages not within the Net Mask are sent to the router. Changing this value when a fixed address is specified causes an automatic restart of the ethernet port, this can be up to 4 seconds. |
| 123 | Net Mask byte 2 | 0-255 |  |
| 124 | Net Mask byte 3 | 0-255 |  |
| 125 | Net Mask byte 4 | 0-255 |  |
| 126 | Limit Client IP addresses |  | Allows the IP addresses that are allowed to connect to be limited. 0x0000 = All client IP address are accepted bit 0 set = Accept IP addresses in range 0 bit 1 set = Accept IP addresses in range 1 etc bit 15 set = Accept IP addresses in range 15 NB This is checked on each read write attempt 208 defines which of these ranges resets the PLC Control Timeout (see 111) |

| 127 | Range 0, Byte A | 0-255 | Only relevant if bit 0 of “Limit Client IP Addresses” is set. Range 0, The first to last addresses acceptable in the range A.B.C.D to A.B.C.E. eg 192.168.1.10 to 10 eg 192.168.1.10 to 19 |
| --- | --- | --- | --- |
| 128 | Range 0, Byte B | 0-255 |  |
| 129 | Range 0, Byte C | 0-255 |  |
| 130 | Range 0, Byte D | 0-255 |  |
| 131 | Range 0, Byte E | 0-255 |  |
| 132 | Range 1, Byte A | 0-255 | Only relevant if bit 1 of “Limit Client IP Addresses” is set. Range 1, The first to last addresses acceptable in the range A.B.C.D to A.B.C.E. |
| 133 | Range 1, Byte B | 0-255 |  |
| 134 | Range 1, Byte C | 0-255 |  |
| 135 | Range 1, Byte D | 0-255 |  |
| 136 | Range 1, Byte E | 0-255 |  |
|  | Etc |  |  |
| 202 | Range 15, Byte A | 0-255 | Only relevant if bit 15 of “Limit Client IP Addresses” is set. Range 15, The first to last addresses acceptable in the range A.B.C.D to A.B.C.E. |
| 203 | Range 15, Byte B | 0-255 |  |
| 204 | Range 15, Byte C | 0-255 |  |
| 205 | Range 15, Byte D | 0-255 |  |
| 206 | Range 15, Byte E | 0-255 |  |
| 207 | LED Test | 0-4 | 0: No testing 1: All six status LEDs Green 2: All six status LEDs Red 3: All six status LEDs Yellow 4: All six status LEDs cycle |
| 208 | PLC Control Connections | Bits 0-15 | Used in conjunction with 126 to define which connections reset the PLC Control Timeout timer. 0x0000 = all allowed IP addresses and RS485 Modbus message reset the PLC Control Timeout timer. Bit 0 set = Modbus message from Range 0 connection resets the PLC Control Timeout timer. Bit 1 set = Range 1 connection resets timer If 208 is non zero then RS485 Modbus messages do not reset the PLC Control Timeout timer. |

## GembusHub Info

These registers are read only.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 500 | Version byte 1 | 1-4 | 1 is a development version 2 is a alpha site release 3 is a beta site release 4 is a full release |
| 501 | Version byte 2 | 60 | 60 Identifies GembusHub |
| 502 | Version byte 3 | 0-255 | Major change count |
| 503 | Version byte 4 | 0-255 | Minor change count. Reset after a major change. |
| 504 | Software Checksum (LSW) |  | Allows code verification against the release paperwork |
| 505 | Software Checksum (MSW) |  |  |
| 506 | For future use |  | If writing to, write a 0 to maintain future compatibility |
| 507 | For future use |  | If writing to, write a 0 to maintain future compatibility |
| 508- 510 | Mac Address | 6 bytes of 0-255 | Mac Address typically written in Hexadecimal eg 00-04-A3-12-34-56. Stored as: 0x0400, 0x12A3, 0x5634 |
| 511 | Status flags |  | Bit 0: Date and time update required Bit 1: Network cable not present Bit 2: PLC Control Timeout Bit 3: No longer used: Was: “Some key Ethernet Settings have changed since power on. Reboot may be required to implement these changes.” Bit 4: Set while there are CRC errors on the Serial Flash chip. Occasional blips can be ignored. Bit 5: Bit 6: Bit 7: Bit 8: Bit 9: Bit 10: Bit 11: Bit 12: Bit 13: Bit 14: Bit 15: |
| 512 | More Status flags |  | Bits 0-3 are the same bits as register 1101. Bit 0: Port 1 Link Status = 0, no valid message received during scan = 1, valid message(s) received during scan Bit 1: Port 2 Link Status (see Port 1 Link Status) Bit 2: Port 3 Link Status (see Port 1 Link Status) Bit 3: Port 4 Link Status (see Port 1 Link Status) Bit 4: Bit 5: Bit 6: Bit 7: Bit 8: Bit 9: Bit 10: Bit 11: Bit 12: Bit 13: Bit 14: Bit 15: |
| 513 | Gemstart Hub IP Address |  | The IP address used for the GembusHub. This may have been allocated by the DHCP or have been fixed in the GembusHub settings. |
| 514 | Gemstart Hub IP Address |  |  |
| 515 | Gemstart Hub IP Address |  |  |
| 516 | Gemstart Hub IP Address |  |  |
| 517 | Router IP address |  | The IP address of the router as defined in the fixed GembusHub settings or as informed by the DHCP. |
| 518 | Router IP address |  |  |
| 519 | Router IP address |  |  |
| 520 | Router IP address |  |  |
| 521 | Net Mask |  | The Net Mask for this network as defined in the fixed GembusHub settings or as informed by the DHCP. |
| 522 | Net Mask |  |  |
| 523 | Net Mask |  |  |
| 524 | Net Mask |  |  |
| 525 | Power LED |  | Each register is split into high and low bytes. Low byte: 0 = LED off 1 = Green - see high byte for number of flashes 2 = Yellow - see high byte for number of flashes 3 = Red - see high byte for number of flashes 4 = Slow 3 way cycle (1s each): G, Y, R 5 = Fast 3 way cycle (500ms each): G, Y, R 6 = 4 way cycle (500ms each): G, Y, R, Off 7 = 2 way cycle (500ms each): Y, G 8 = 2 way cycle (500ms each): Y, R High byte only applies if low byte is 1, 2 or 3: 0 = Solid colour 1 = Not used 2-10 = The number of flashes (300ms on, 200ms off, 1s between sequences) 11 = Slow flash (1s on, 1s off) 12 = Fast flash (100ms on, 100ms off) NB Not all options are used by GembusHub. |
| 526 | Network LED |  |  |
| 527 | Gembus 1 LED |  |  |
| 528 | Gembus 2 LED |  |  |
| 529 | Gembus 3 LED |  |  |
| 530 | Gembus 4 LED |  |  |

## GembusHub Statistics

Write the registers to zero to reset them.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 600 | Ethernet Tx Count | 0-65535 |  |
| 601 | Ethernet Rx Count | 0-65535 |  |
| 602 | Ethernet Tx Errors | 0-65535 |  |
| 603 | Ethernet Rx Errors | 0-65535 |  |
| 604 | Controlling device timeout | 0-65535 | Number of times that there has been no message from the PLC via the Ethernet port or a RS485 Modbus port for the PLC Control Timeout period. NB Only increments once for each loss of control |
| 605 | GembusHub Power On counter | 0-65535 | Retained and incremented after a power cycle. |
| 606 | GembusHub Watchdog count | 0-65535 | Increments every 100ms to confirm link connection |
| 607 | Run Time Errors |  | If incrementing then report back to supplier. |
| 608 | Modbus Format Errors |  |  |
| 609 | Modbus Address Errors |  |  |
| 610 | Modbus Length Errors |  |  |
| 611 | Modbus CRC Errors |  |  |
| 612 | Modbus Illegal Function Exceptions (Exception 1) |  |  |
| 613 | Modbus Illegal Address Exceptions (Exception 2) |  |  |
| 614 | Modbus Illegal Value Exceptions (Exception 3) |  |  |
| 615 | Modbus Write Exceptions (Exception 4) |  |  |
| 616 | Modbus Buffer Errors |  |  |
| 617 | Modbus Replies |  |  |
| 618 | Ethernet Invalid Clients Accesses |  | A client with an IP address not in the defined IP address range has accessed this device, The message was ignored. |
| 619-622 | The invalid IP address trying to access GembusHub |  | The invalid IP address trying to access GembusHub |
| 623 | Rejected Connection Port |  | The port the Invalid IP has tried to connect to. Normally this will be the Modbus port. Added in GembusHub version 4.60.1.10 |
| 624 | Modbus TCP/IP Active connections |  | The number of Modbus connections that are currently active |
| 625 | Modbus TCP/IP Rx while Tx errors |  | Indicates that the client is not waiting for a reply before sending the next request |
| 626 | Modbus TCP/IP Total Connections |  | Increments each time a connection is made |
| 627 | Modbus TCP/IP Transmits |  | Number of messages transmitted |
| 628 | Modbus TCP/IP Retransmits |  | Number of messages that were not ACKed and had to be retransmitted |
| 629 | Modbus TCP/IP Total ACKs |  | Number of ACKed transmissions (and retransmissions) |
| 630 | Modbus TCP/IP Receives |  | Number of messages received |
| 631 | Modbus TCP/IP Timeouts |  | Number of TCP/IP timeouts |
| 632 | Modbus TCP/IP Connections Closed |  | Number of times a connection has been closed |
| 633 | Modbus TCP/IP Connections Aborted |  | Number of times a connection has been aborted |
| 634 | Modbus TCP/IP New IPs |  | Number of times the IP address of GembusHub has been changed by the DHCP |
| 635 | Serial Flash Chip writes |  | The number of writes to the serial flash chip. This will update when non volatile configuration or data is changed. Also updated when run time errors occur. |
| 636 | Serial Flash CRC Errors |  | The number of CRC errors on the data read back from the serial flash chip. If this is incrementing every 10s or so then there is a hardware fault on the flash chip. |

# Gembus Registers

These registers are repeated for each of the 4 ports. A different unit address (0x11-0x14) is used for each port (1-4).

If one or more of the RS485 ports is set to Modbus slave then the relevant data map will still be present but mostly not used or updated. Only the registers with a “Modbus Slave” description are valid. I.e. Baud Rate at address 1002 and the message counts at 1102 and 1103. All other registers are undefined.

## Link Settings

Define the parameters for how the link operates. These settings are retained through a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1000 | GembusHub Port Number | 1-4 | Read Only. Identifies the hardware port that is being configured. A write to this register with the wrong value will cause the whole message to be ignored. Retained through a power cycle. |
| 1001 | Gemstart Link Number | 0-15 | R/W. The id used to confirm the link number to Gemstart. The Gemstart address consists of the link number and the Gemstart number 00-99 eg 123 is Gemstart 23 on link 1. Links 10 to 15 are displayed as A to F on Gemstart. Retained through a power cycle. |
| 1002 | Baud Rate / 100 | 3, 6 , 12, 24, 48, 96, 192, 384 | R/W. The baud rate divided by 100. Not all rates will be supported by every Gemstart. Pick a rate that is common to every Gemstart on the link. Eg 19200. Higher baud rates limit the link length. Retained through a power cycle. Set the highest baud rate that does not cause the Timeouts count (1106) to increment. |
| 1003 | First Gemstart Address | 00-99 | R/W. Define the scan range for this link of Gemstarts. Must be <= Last Gemstart Address Retained through a power cycle. |
| 1004 | Last Gemstart Address | 00-99 | R/W. Define the scan range for this link of Gemstarts. Must be >= First Gemstart Address Retained through a power cycle. |
| 1005 | Config Conflict Master | 0-4 | R/W. 0 = No master. A fault is flagged by Gemstart and must be resolved manually. 1 = Unit Master. The GembusHub configuration is updated from the Gemstart. 2 = Host (GembusHub) Master. The Gemstart configuration is updated from GembusHub. 3 = Host (GembusHub) Read Only. Any config changes received from the Gemstart are ignored and the GembusHub configuration is written back to Gemstart. 4 = Maintenance. Configuration is never supplied by GembusHub which avoids Configuration conflicts. Configuration is read from Gemstart. Retained through a power cycle. |
| 1006 | No Reply Timeout Limit | 0-255 | R/W. This parameter contains the maximum fail count. I.e. The number of consecutive scans that a Gemstart does not reply before the unit is flagged as offline. The default value of 10 will be used if 0 entered. Retained through a power cycle. |

### Broadcast Control

Enable to get GembusHub to send a broadcast command as soon as the command is written to the command array. Not all Gemstarts will understand the broadcast command. Has the advantage of getting the command out to lots of Gemstarts as quickly as possible. Disadvantage is that it slows down the scan time slightly.

Retained through a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1007 | Fast Command Broadcasts | 0-1 | R/W 0 = Disabled. 1 = Enabled. In this mode a broadcast message is sent when GembusHub detects a change in the command to any Gemstart. This reduces the time taken to get the command from the PLC to Gemstart. Gemstart 4.3 F6 and Gemstart 4.2 F4 or later action these messages. |

### Continuous Data Request Control

Define the amount of data to request from the Gemstarts. Reducing the amount of data speeds up the scan time. Reducing the data size will leave the old data unchanged unless the Gemstart goes off line. If is up to the process to ensure the all data used is reasonably fresh.

Retained through a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1008 | Input Data Size Requested | 0-3 | Defines the size of the data requested from each Gemstart. Changing this does not affect the memory map size. Use a smaller size to reduce the Gemstart scan time. - 0 = 2 status registers requested (Normal); - 1 = 1 status register requested (Short); - 2 = 3 status registers requested (Long); - 3 = 8 status registers requested (Long + Grp10) This allows the data size required to be changed dynamically to speed up the link of needed without having to remap all the data. |

## Link Statistics

Write the registers to zero to reset them.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1100 | Configuration Error |  | 0 = Ok 1 = Wrong port number written (previous settings restored) 2 = Gemstart link number out of range (previous settings restored) 3 = Baud rate out of range (9600 used) 4 = First Gemstart address out of range (0 used) 5 = Last Gemstart address out of range (99 used) 6 = Last Gemstart address not after first address (99 used) 7 = Config Conflict out of range (No master used) 8 = “No reply” timeout limit out of range (10 used) |
| 1101 | Link Status of all 4 Ports |  | Bits 0-3 are the same bits as register 512. Bit 0: Port 1 Link Status = 0, no valid message received during scan = 1, valid message(s) received during scan Bit 1: Port 2 Link Status (see Port 1 Link Status) Bit 2: Port 3 Link Status (see Port 1 Link Status) Bit 3: Port 4 Link Status (see Port 1 Link Status) |
| 1102 | Tx count (LSW) Modbus Slave: Rx Count |  | The number of messages transmitted. |
| 1103 | Tx count (MSW) Modbus Slave: Tx Count |  |  |
| 1104 | CRC Errors |  | The number of corrupted replies. |
| 1105 | Last unit with CRC error |  | The address of the last reply that was corrupted. |
| 1106 | Timeouts |  | The number of short replies or no replies when a unit is online. No replies from offline units are ignored. (Does not include CRC errors) |
| 1107 | Last unit with Timeout error |  | The last unit to reply with a corrupted message or to not respond with a reply when it is online. No replies from offline units are ignored. |
| 1108 | Number of Gemstart replies in scan |  | The number of good replies received during the last scan |
| 1109 | Last Scan Time |  | Scan time in ms |
| 1110 | Average Scan Time |  | Weighted average scan time in ms |
| 1111 | Max Scan Time |  | Max scan time in ms since setting was last reset. |

## Gemstart Status Flags

Read only status bits accessible via registers. Each register contains 16 flags with 1 flag per Gemstart.

NB The Config Changed, Data Changed and Link Control flags are all cleared on reading. If two or more clients are reading these flags then only one of the clients will see a flag set. The use of these flags should therefore be considered carefully.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1200 to 1206 | Online flag |  | 100 bits, 1 bit per Gemstart. 16 bits per register. Bit 0 of register 1300 is for Gemstart 0. Bit 2 of register 1306 is for Gemstart 99. |
| 1207 to 1213 | Config changed flags |  | 100 bits, 1 bit per Gemstart. 16 bits per register. Set if the configuration for a unit has been changed by Gemstart. Reset on reading these flags, |
| 1214 to 1220 | Data changed flags |  | 100 bits, 1 bit per Gemstart. 16 bits per register. Set if the contactor has changed state or if the fault present flag has changed. Reset on reading these flags, |
| 1221 | Link Control flags |  | Bit 0. Set when an immediate Group Control message has been sent. Reset on reading these flags, Bit 1. Set when Single Data Request has completed (may be successful or with error). Reset on reading these flags, Bit 2. Set when a fast command broadcast has been sent. Reset on reading these flags. |

## Link Controls

The Link Control Registers are a block of parameters used to provide data exchange facilities under the PLC program control. Separate control registers are available for Group Control and Data Request.

The Link Control registers are reset to zero by a power cycle.

### Group Control

The group control register allows a group of Gemstarts to be started and stopped at the same time with a single broadcast command. If bit 15 is set then when the register changes a broadcast command is sent immediately. The group command is also send in every restart message regardless of the state of bit 15.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1300 | Group Control |  | Bits 0-3: Gemstart command Bit 8: Group 1 flag. When set the Group 1 Gemstarts will use the command in bits 0-3. Bits 9-14: As bit 8 but for groups 2 to 7. Bit 15. Send immediately. |
| 1301 | For future use |  | If writing to, write a 0 to maintain future compatibility |
| 1302 | For future use |  | If writing to, write a 0 to maintain future compatibility |

### Single Data Request

Set the Target Address and Target Data Type in the same write message. Then read the Link Control Operations flags and/or read the Request Status. Once the Request Status is “Completed” the Requested Data Address, Type, Data and length will be valid. NB It’s ok to read the Request Status and the Requested Data area in a single message and use the Requested Data if the Request Status is completed.

Writing to the Target Address and/or Target Data Type will always restart the request cycle.

Registers 1306 to 1319 will be set to 0 as soon as a request is started and will only become valid when the Request Status changes to Completed.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 1303 | Target Address | 0-99 | The address of the unit to be read |
| 1304 | Target Data Type | 0-10 | Data type to request: 0 Static Data 1 Group Data 1 2 Group Data 2 3 Group Data 3 4 Group Data 4 5 Group Data 5 6 Group Data 6 7 Group Data 7 8 Group Data 8 9 Group Data 9 10 Group Data 10 |
| 1305 | Request Status |  | Read only. Automatically changes to 1, Busy, when Target Address or Target Data Type are written to. 0 No data requested 1 Busy 2 Completed (the following 13 registers are valid) 3 Unit Not Present 4 Request failed 7 Target outside scan range 8 Request timed out |
| 1306 | Requested Data Address |  | Read only. The address of the unit that supplied the data |
| 1307 | Requested Data Type |  | Read only. The type of data supplied by the Gemstart. The same codes as for the Data Request Type are used. |
| 1308 to 1318 | Requested Data |  | Read only. Up to 11 registers of data depending on the request type. Static data uses 11 registers and Group data uses 5 registers. Unused registers are written to 0. |
| 1319 | Requested Data Length | 0 - 11 | Read only. The number of registers (1308 to 1318) updated with data from the Gemstart. The remaining registers will have been zeroed. Added in GembusHub version 4.60.1.10 |

Timing

A Single Data Request is only sent out on “even” scans i.e. every other scan. Gemstart will reply with the data on the next scan. The data is immediately available in the registers.

Best Case Timing	1 scan (see 1110)

Worst Case Timing	3 scans (see 1110)

## Output Command Array

One register per Gemstart.

The Output Command registers are reset to 0x03, No Action, after a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 2000 | Output command for Gemstart 0 |  | See the Gemstart manual for a definition of the command register. Bits 0-3 sent in the command message. If bits 8 to 15 are non zero they are sent in an additional data byte added to the message. |
| To |  |  |  |
| 2099 | Output command for Gemstart 99 |  |  |

After issuing a command the controlling device should set the command register to 0x03 after a small delay, or when feedback confirms that the command has been actioned.

## Input Data Array

Eight registers per Gemstart are allocated. The amount of data read from each Gemstart is defined in the Continuous Data Request setting. All 8 registers are cleared out and the Not Responding status (1) is loaded into the status word if the Gemstart goes offline. Other than that any old data is not cleared out if the Continuous Data request size is reduced. It is up to the application to ensure that old data is not assumed to be current.

To allow for easy access to useful data there are a number of address maps that can be used to read selective data from the Input data.

From 3000 length 800 – the full data map of all the data from all the Gemstarts.

From 3800 length 100 – the Status Word for each of the Gemstarts

From 3900 length 100 – the Load Word for each of the Gemstarts

From 4000 length 100 – the Fault Code for each of the Gemstarts

From 4100 length 200 – the Status Word and Load Value for all 100 Gemstarts

From 4300 length 300 – the Status Word, Load Value and Fault Code for all 100 Gemstarts

All status registers are read only.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 3000 | Gemstart 0 Status Word |  |  |
| 3001 | Gemstart 0 Load Value |  |  |
| 3002 | Gemstart 0 Fault Code |  |  |
| 3003 | Gemstart 0 Group 10 Word 1 |  |  |
| 3004 | Gemstart 0 Group 10 Word 2 |  |  |
| 3005 | Gemstart 0 Group 10 Word 3 |  |  |
| 3006 | Gemstart 0 Group 10 Word 4 |  |  |
| 3007 | Gemstart 0 Group 10 Word 5 |  |  |
| 3008- 3015 | Gemstart 1 Data |  |  |
| Etc |  |  |  |
| 3792 3799 | Gemstart 99 Data |  |  |

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 3800 | Gemstart 0 Status Word |  |  |
| 3801 | Gemstart 1 Status Word |  |  |
| Etc |  |  |  |
| 3899 | Gemstart 99 Status Word |  |  |

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 3900 | Gemstart 0 Load Value |  |  |
| 3901 | Gemstart 1 Load Value |  |  |
| Etc |  |  |  |
| 3999 | Gemstart 99 Load Value |  |  |

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 4000 | Gemstart 0 Fault Code |  |  |
| 4001 | Gemstart 1 Fault Code |  |  |
| Etc |  |  |  |
| 4099 | Gemstart 99 Fault Code |  |  |

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 4100 | Gemstart 0 Status Word |  |  |
| 4101 | Gemstart 0 Load Value |  |  |
| 4102 | Gemstart 1 Status Word |  |  |
| 4103 | Gemstart 1 Load Value |  |  |
| Etc |  |  |  |
| 4298 | Gemstart 99 Status Word |  |  |
| 4299 | Gemstart 99 Load Value |  |  |

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 4300 | Gemstart 0 Status Word |  |  |
| 4301 | Gemstart 0 Load Value |  |  |
| 4302 | Gemstart 0 Fault Code |  |  |
| 4303 | Gemstart 1 Status Word |  |  |
| 4304 | Gemstart 1 Load Value |  |  |
| 4305 | Gemstart 1 Fault Code |  |  |
| Etc |  |  |  |
| 4597 | Gemstart 99 Status Word |  |  |
| 4598 | Gemstart 99 Load Value |  |  |
| 4599 | Gemstart 99 Fault Code |  |  |

As it is not always clear how many status registers have been updated the next set of registers tells you how many registers were written on the last successful update. The value is cleared to 0 if the unit goes offline.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 4600 | Gemstart 0 registers written | 0,1,2,3 or 8 | Confirms the amount of data being written to the status registers. |
| 4601 | Gemstart 1 registers written |  |  |
| Etc |  |  |  |
| 4699 | Gemstart 99 registers written |  |  |

## Configuration Data

One Gemstart’s configuration is 128 registers long but only 123 registers can be read at a time. Removing the change count bytes from the configuration allows the configuration to be read as 120 registers. You must read the whole configuration for one and only one Gemstart at one time.

The register address’s increase by 1 for each Gemstart. So reading address 5000 length 120 gets all of Gemstart 0’s configuration. Read from address 5010 and get all of Gemstart 10’s configuration. Reading length 121 will return the configuration data and the CRC register.

Writing 120 registers of config to GembusHub will update Gemstart if it is present. Writing config will clear a Config Conflict.

Writing to the configuration registers with all zeroes will cause GembusHub to requests the configuration from Gemstart. It will take 36 Gemstart scans to read the configuration from Gemstart. Read the change counts to monitor progress. When all 16 change counts are all non zero then the configuration has been read.

The configuration data for all 400 Gemstarts is retained in GembusHub through a power cycle.

| Register | Description | Range | Comments |
| --- | --- | --- | --- |
| 5000 | Gemstart 0 Config |  | Read length 120 registers to get 16 pages of 15 bytes each. Read length 121 registers to get the CRC as well. |
| 5001 | Gemstart 1 Config |  | As above |
|  | Etc |  | As above |
| 5099 | Gemstart 99 Config |  | As above |

### Config CRCs

Read from register 5100 to 5199 to get some or all of the Config CRCs. This CRC value should match the value displayed on GEMPRO or the HHP. Writing to the Config CRCs is not allowed. The Config CRCs are retained through a power down.

| 5100 | Gemstart 0 Config CRC |  | The CRC of bytes 0 to 14 of pages 0 to 14 of the configuration area. Should be the same value displayed by the HHP/GEMPRO. |
| --- | --- | --- | --- |
| 5101 | Gemstart 1 Config CRC |  | As above |
|  | Etc |  | As above |
| 5199 | Gemstart 99 Config CRC |  | As above |

### Configuration Change Counts

Read from address 5200 to 5999 to get the change counts for each Gemstart. There are 16 changes count bytes packed into 8 registers for each Gemstart. Gemstart 0 starts at address 5200, Gemstart 1 at address 5208 etc. You cannot write to the Change Counts registers. The Change Counts are retained through a power down.

| 5200 to 5207 | Gemstart 0 Config Change Counts |  | Read 8 registers to get the 16 change counts for 1 Gemstart. |
| --- | --- | --- | --- |
| 5208 to 5215 | Gemstart 1 Config Change Counts |  | As above |
|  | Etc |  | As above |
| 5992 to 5999 | Gemstart 99 Config Change Counts |  | As above |

### Gemstart Type

GembusHub’s best guess as to what type of Gemstart the loaded configuration belongs to. If it can’t determine which type of Gemstart it is the EPROM number is shown. Read only registers.

Note: Only updated when page 15 of the config is read from the Gemstart. Stored in non volatile memory. Write 0 to the Gemstart Type to clear the last known setting. As this is non volatile memory writing should not be a regular activity.

| 6000 | Gemstart 0 Type | The type of Gemstart configuration. 0 = Unknown 10 = Gemstart 1 20 = Gemstart 2 30 = Gemstart 3 31 = Enhanced Gemstart 3 41 = Gemstart 4.2 42 = Gemstart 4.2E 43 = Gemstart 4.3 50 = Gemstart 5 If the Gemstart type cannot be determined but there is an EPROM number present (GS4 or GS5 config) then the 4 digit EPROM number is returned in this location. |
| --- | --- | --- |
| 6001 | Gemstart 1 Type | As Above |
| 6099 | Gemstart 99 Type |  |

## Development Data

Data useful for debugging faults during and after development. These may be indications of unusual occurrences or unexpected values encountered by the code etc. It is not expected that these tables will normally be accessed. If read then access using station address 16.

| Register | Description | Comments |
| --- | --- | --- |
| 7000 | Run Time indication count | Indication of how many run time indications are occurring |
| 7001 | Run Time indication line number | The line number in the file of the run time indication |
| 7002- 7009 | Run Time indication file name | Up to 16 characters of the file name for the last run time indication. |

## Scratchpad

A free area of 512 non-volatile registers on device 16, address 9000 is available for general useage. Any data written to these registers will be maintained across a power cycle. Data can be read and written freely although registers that will change more that 1 million times should be avoided as the non-volatile ram may start to fail.

| Register | Description | Comments |
| --- | --- | --- |
| 9000 to 9511 | For general data storage | Non-volatile scratchpad memory. Not used by GembusHub but made available for attached devices to freely read and write any data required. |